## Table of Contents
4.1 | Baseline Data and System Assessment
4.1.a | A description of any currently used internal baseline and system assessment practices (such as system reliability baseline, system asset health baseline, etc.) that includes:
4.1.a.i | Method and tools used to develop the baseline and assessment |  | KEY
4.1.a.ii | Forecasting time horizon(s) |  | Distribution traditional data
4.1.a.iii | Key performance metrics |  | Net Metering & Qualified Facility
4.1.b | A summary of the utility’s distribution system assets including: |  | Electric Vehicle
4.1.b.i | Asset classes |  | Demand Response
4.1.b.v | Number of assets in each class |  | OPUC filed reports
4.1.b.ii | Average age of assets in each class
4.1.b.iii | Age range of assets in each class
4.1.b.iv | Industry life expectancy of assets in each class
4.1.c (SCADA) | A discussion of distribution system monitoring and control capabilities including:
4.1.c.i | Number of feeders
4.1.c.ii | Number of substations
4.1.c.iii | Monitoring and control technologies (such as SCADA, AMI, etc.) currently installed, and the percentage of substations, feeders, and other applicable equipment with each technology
4.1.c.iv | A description of the monitoring and control capabilities (for example, percentage of system with each technology, resulting capacity, such as remote fault detection or power quality monitoring, and what time interval measurements are available)
4.1.c (AMI) | A discussion of distribution system monitoring and control capabilities including:
4.1.c.i | Number of feeders
4.1.c.ii | Number of substations
4.1.c.iii | Monitoring and control technologies (such as SCADA, AMI, etc.) currently installed, and the percentage of substations, feeders, and other applicable equipment with each technology
4.1.c.iv | A description of the monitoring and control capabilities (for example, percentage of system with each technology, resulting capacity, such as remote fault detection or power quality monitoring, and what time interval measurements are available)
4.1.d | A discussion of any advanced control and communication systems (for example: distribution management systems, distributed energy resources management systems, demand response management systems, outage management systems, field area networks, etc.). Include a description of system visibility and capabilities, the percentage of system reached with each capability, the percentage of customers reached with each capability, and any utility programs utilizing each capability.
4.1.e | Historical distribution system spending for the past five years, in each category:
4.1.e.i | Age-related replacements and asset renewal
4.1.e.ii | System expansion or upgrades for capacity
4.1.e.iii | System expansion or upgrades for reliability and power quality
4.1.e.iv | New customer projects
4.1.e.v | Grid modernization projects
4.1.e.vi | Metering
4.1.e.vii | Preventative maintenance
4.1.f | Net Metering and Small Generator information:
4.1.f.i | Total existing net metering facilities and small generator facilities interconnected to the distribution grid (or to the transmission system, as appropriate for small generator facilities) at time of filing, by feeder.
4.1.f.i.1 | The total number of net metering facilities by resource type
4.1.f.i.2 | The total estimated rated generating capacity of net metering facilities by resource type
4.1.f.i.3 | The total number of small generator facilities by resource type
4.1.f.i.4 | The total nameplate capacity of small generator facilities by resource type
4.1.f.ii | The total number and nameplate capacity of queued net metering facilities and small generator facilities at time of filing, by feeder, broken down by resource type
4.1.f.iii | A map, in electronic format, identifying locations of net metering facilities and small generator facilities interconnected to the distribution grid (or to the transmission system, as appropriate for small generator facilities) at time of filing.
4.1.g | Total number of electric vehicles (EVs) of various sizes served by the utility's system at time of filing
4.1.h | Number of EVs added to the utility's system in each of the last five years
4.1.i | Total number of charging stations on the utility's system, broken down by type, ownership, and feeder
4.1.j | Total number of charging stations added to the utility's system in each of the last five years, broken down by type
4.1.j.1 | Data on the availability and usage patterns of charging stations
4.1.l | A high-level summary of demand response (DR) pilot and/or program performance metrics for the past five years including: (For example, see Table 26 on page 101 of Appendix 1 of 2019 PGE Smart Grid Report, https://edocs.puc.state.or.us/efdocs/HAQ/um1657haq15635.pdf)
4.1.l.i | Number of customers participating by residential and business customer class, and combined total
4.1.l.ii | By winter and summer demand response season:
4.1.l.ii.1 | Maximum available capacity of DR by residential and business customer class, and combined total
4.1.l.ii.2 | Season system peak
4.1.l.ii.3 | Available capacity of DR, expressed as a percentage of the season system peak
4.1.m - NM | Plans should include the utility's most recently filed Annual Net Metering Report and the most recently filed Annual Small Generator Report, each as an appendix to the Plan. (link is for 2020 numbers)
4.1.m - SGR | Plans should include the utility's most recently filed Annual Net Metering Report and the most recently filed Annual Small Generator Report, each as an appendix to the Plan. (link is for 2019 numbers, 2020 numbers out on 5/29/2021)
4.1.n | Plans should include the utility's most recently filed Annual Reliability Report as an appendix to the Plan. Any descriptions of reliability challenges and opportunities in the Distribution System Plan should cross-reference underlying data and information contained in the Annual Reliability Report. (link is for 2020 numbers)
4.5 | As Part of its Part 1 filing each utility should prepare for the upcoming transition period and include a high-level summary to discuss: | TBD
4.5.a | How legacy distribution planning practices will be transitioned to the requirements of Part 2 | TBD
4.5.b | Whether all legacy distribution planning practices will be transitioned in time for filing Part 2, and if not, the expected timeframe for that eventual transition | TBD
4.5.c | Efforts to synchronize IRP activities with requirements of Part 2 | TBD

## Baseline 4.1.a.i & ii
UM 2005/DSP Requirement
4.1.a | A description of any currently used internal baseline and system assessment practices (such as system reliability baseline, system asset health baseline, etc.) that includes:
4.1.a.i | Method and tools used to develop the baseline and assessment
4.1.a.ii | Forecasting time horizon(s)
| Table of Contents | Distribution Forecasting dataset as of Jan 2021
|  | 4.1.a.i & ii | 4.1.a.i
|  | PURPOSE This document provides criteria and methods related to performing Distribution Planning Studies utilized as a basis for future project justification and development. BASE CASE VALIDATION The base case is to be developed via the use of CYME Modeling software. The CYME base case must be validated prior to evaluating the system under normal conditions (N-0) and running N-1 contingency studies. To develop a base case, a common case is to be chosen, and updated by Distribution Planning Engineers. Each Distribution Planning Engineer is responsible for updating line and equipment configuration, and addressing CYME generated errors in their assigned regions. Updates are then compiled into a single database to be used for designated studies. Internal PGE tools used for base case development are the T&D Standards, GIS, Autodesk Vault, eRecords, PI ProcessBook and the T&D Database. Some of the more common corrections to be made are: • Feeder breaker designations • Breaker and bus voltage designations • Transformer LTC set point voltages • Transformer LTC R&X settings • Capacitor bank sizes and voltages • Transformer and feeder regulator settings • Feeder line type validation • Feeder line phasing validation BASE CASE ANALYSIS A report can be generated in CYME to identify base case loading and voltage violations. Also, the CYME display can be utilized to physically locate these base case loading and voltage violations. These violations are documented and have the highest priority for developing mitigation plans. DESIGN CRITERIA PGE’s system is designed to serve existing customer loads with adequate reserved capacity to pick up that load in the event of a failure. In the near term distribution planning studies, failures will be limited to the loss of a distribution power transformer or a distribution feeder. Planning design criteria for PGE’s distribution power transformers requires the transformers not to exceed 80% of their seasonal loading beyond nameplate ratings (LBNR) under normal operation (N-0) during a peak period. Limiting components include the transformer windings, load tap changers, bushings, leads, and voltage regulators. In the event of a transformer related failure or outage (N-1), nearby transformers from either the same or adjacent distribution substations shall be able to pick up the load. Planning design criteria for PGE’s distribution feeders require associated feeder getaways, mainlines, and voltage regulators not to exceed 67% of their normal seasonal thermal ratings. For most general use feeders, this equates to either 2/3 normal capacity of a standard feeder mainline, or 12 MVA. DESIGN CRITERIA EXCEPTIONS There are some exceptions to the planning design criteria for distribution power transformers and for distribution feeders. These exceptions allow for equipment to load to levels beyond the recommended design criteria under normal (N-0) operation. DEDICATED TRANSFORMERS For distribution power transformers dedicated to a single customer, loading can reach 100% of seasonal LBNR under normal (N-0) configuration. For dedicated transformers, in the event of an outage there is a contingency or a load shedding scheme that will prevent PGE transformers from loading beyond their LBNR. DEDICATED FEEDERS Dedicated feeders may be loaded up to 100% of their normal seasonal thermal ratings under normal (N-0) configuration. For these feeders, a contingency or load shedding scheme will prevent the feeders from exceeding these limits. ALTERNATE SERVICE Alternate service agreements affect the operation of general use distribution power transformers and distribution feeders. An alternate service customer is generally served by a single feeder. In the event of an outage to the customer’s preferred feeder, the customer will automatically transfer to an alternate feeder. PGE is contractually bound to reserve adequate capacity for alternate service customers. A transformer or a feeder that is designated as an alternate source shall at all times have reserved capacity to pick up the agreed upon load as stated in the corresponding alternate service agreement. For a transformer designated as source for alternate service, the sum of the transformer’s peak load and the reserved capacity must be equal to or less than the transformer’s LBNR. For a feeder designated as a source for alternate service, the sum of the feeder’s peak load and the reserved capacity must be equal or less than the feeder’s normal thermal limit. SECONDARY NETWORK FEEDERS Secondary networks are designed to allow customers to be served by a group or “system” of dedicated feeders. Secondary conductors are interconnected to serve pockets of load in common areas. Feeders in these network systems are allowed to be taken out of service one, and in some cases two at a time for planned or unplanned outage scenarios. With this redundancy in place, secondary network feeders and corresponding transformers are individually lightly loaded so that they have the capacity to pick up load from a transformer or feeder serving the same network load. Due to their complex nature, secondary network feeders are modeled in PowerWorld. STUDY CRITERIA Two categories of studies are analyzed: N-0 base case and N-1 contingency. An N-0 base case corresponds to a normal operating condition; all feeders and distribution power transformers are in service. An N-1 contingency corresponds to an abnormal condition; a single component is out of service (e.g., distribution power transformer, distribution feeder). Contingencies will be limited to the distribution power transformer and to the distribution feeder. Initial near term studies will incorporate peak summer conditions. PGE’s system is modeled to utilize a five-year projected 1-in-3 system loading as shown in the PGE load forecast. For a base case scenario, the distribution system is configured in an operational state with the addition of approved Capital Funding Projects included in the system model. Distribution loading is allocated at the distribution power transformer level per substation. FEEDER SWITCHING For N-1 contingency, all field devices utilized for restoration must be load break three-phase gang operated switches or three phase reclosers. If required, devices utilized for restoration in distribution substations must be three-phase circuit breakers or circuit switchers. Other means that may be used for switching in the field (closing single phase jumpers, closing cable disconnects, operating non-load breaking devices, etc.) will not be included when performing studies. Field devices allowed to be modeled for switching purposes are overhead devices rated at either 600 or 900 amps, submersible devices rated at 600 amps, and padmounted devices rated at either 600, 900 or 1200 amps. Distribution feeders are split into switchable sections, or zones. Ideally, with feeders limited to 12 MVA, or 67% of their normal thermal ratings, a switchable section shall not exceed 6 MVA. This will allow an entire feeder under contingency (N-1) to be picked up by two adjacent feeders during a peak period. A section located on the load side of a fuse or a recloser without a bypass switch is not considered a switchable section. Due to dense loading, and short length relative to rural or remote feeders, ideally an urban feeder shall require one level of switching to adjacent feeders. This means that during a peak period, service restoration feeders adjacent to the feeder taken out of service shall not be offloaded in order to pick up unserved load. If further action is required, unserved load will be reported. Rural and remote feeders are allowed two levels of switching to adjacent feeders. To pick up unserved load, a feeder can be offloaded to an adjacent feeder. VOLTAGE CRITERIA Distribution voltage requirements allow feeders to vary at a nominal voltage +/- 5%. In CYME, for most feeders, the base nominal delivery voltage is 120 volts. When performing contingency studies for distribution feeders and distribution power transformers, no feeder branch shall be outside of the allowable voltage range. RESULTS Study results will determine which areas of the system need improvements. Initially, small projects are considered to achieve redundancy. These may include feeder balancing, permanent load shifts that can be achieved without upgrades, and small reconductor jobs. The results are analyzed to determine if there are areas of the system, consisting of multiple feeders and/or transformers, which do not have N-1 redundancy. These areas are studied together to determine a project to mitigate multiple redundancy constraints. Detailed studies are performed for feeders and/or transformers that may not meet loading or voltage criteria. These studies are prompted by the following: 1. Base Case loading and voltage violations 2. T&D Design Criteria violations 3. Existing load density 4. Potential future load additions (reference Community Plans where possible) 5. System Performance (Outage history, SAIDI/SAIFI indices) Detailed studies will identify multiple options for each substation. The recommended option should defer additional capital projects at the substation for a minimum of ten years, where possible. High level cost estimates are developed for these options. Options analyses are performed to determine reduced risk and overall system benefits. White papers, and ultimately Capital Funding Projects, are developed as a result of the detailed studies. REPORTING For the N-0 study, voltages outside of bandwidth, transformers loaded at 80% of LBNR or higher, and feeders loaded at 67% of normal thermal limit or higher will be listed and reported. Corrective actions will be required for equipment projected to exceeds 100% of their respective seasonal LBNR or seasonal thermal limits. For N-1 scenarios, voltages outside of bandwidth, transformers loaded at 95% of LBNR or higher and feeders loaded at 95% of normal thermal limits or higher will be listed and reported. Corrective actions will be required for equipment that exceeds 100% of their respective seasonal LBNR or seasonal thermal limits. If possible, corrective actions will solve loading and voltage problems for a general area. After studies are completed, options are analyzed, and corrective actions are identified, a tentative timeline for these corrective actions will be developed. The study process, analyses, results and recommendations are then captured in a formal report. | Annual seasonal load forecasts are for each distribution power transformer are calculated via an in-house program created in Visual Basic. These forecasts utilize a “top down” approach for predicting loads for each of these transformers. Inputs to this tool include: • PGE’s corporate forecast for 1-in-3 peak summer and winter loading • Known load additions or lumped load addition • Historical loading information (five years) for each distribution power transformer • Compensated Power factor for each distribution power transformer during the designated peak period This program factors in historical load growth, and known load additions to scale distribution power transformer loading to the designated load as provided in PGE’s corporate forecast. The program utilizes scaling factors to approximate non-coincidental loading that is provided in historical loading information. Also, external and internal losses are subtracted. Outputs from the program include: • Peak annual seasonal MW and MVAR output for each distribution power transformer • Peak annual seasonal MVA and PF for each distribution power transformer

## Baseline 4.1.a.iii
UM 2005/DSP Requirement
4.1.a.iii | Key performance metrics
| Table of Contents | Asset dataset
|  |  | Excluding MED's |  |  |  | Including MED's
|  |  | SAIDI | SAIFI | MAIFI | CAIDI | SAIDI | SAIFI | MAIFI | CAIDI
|  | 2020 | 99.6889 | 0.59575 | 1.4221 | 167.3323 | 311.9253 | 0.8107 | 1.4221 | 384.7609
|  | 2019 | 98.2938 | 0.61392 | 1.2813 | 160.1088 | 127.8692 | 0.70939 | 1.2813 | 180.2515
|  | 2018 | 88.4711 | 0.51522 | 1.2573 | 171.7148 | 88.4711 | 0.51522 | 1.2573 | 171.7148
|  | 2017 | 112.8551 | 0.62439 | 1.3501 | 180.7453 | 350.0956 | 1.0433 | 1.3501 | 335.5505
|  | 2016 | 97.0263 | 0.59359 | 1.1362 | 163.4557 | 169.3172 | 0.79243 | 1.1362 | 213.6686
|  | Reliability Measure Definitions | [8 empty] | Major Event Day (MED) Definition and Classification
|  | SAIDI is the system average interruption duration index. This is the sustained interruption duration time (in minutes) that an average customer experiences during the year. It is determined by dividing the annual sum of all customer sustained interruption durations by the total number of customers served. SAIDI = Sum of customer sustained interruption durations / Total number of PGE customers served = CAIDI x SAIFI ------------------------------------------------------------------------------------------------------------------------------------------------ SAIFI is the system average sustained interruption frequency index. This index is the number of times that an average customer experiences a sustained interruption during a year. It is determined by dividing the total annual number of customer sustained interruptions by the total number of customers served. SAIFI = Total number of customer sustained interruptions / Total number of PGE customers served = SAIDI / CAIDI ------------------------------------------------------------------------------------------------------------------------------------------------ MAIFI is the momentary average interruption frequency index. This index is the number of times that an average customer experiences momentary interruption events during a year. It is determined by divding the total annual number of customer momentary interruption events by the total number of customer served. Note that this index does not include the events immediately preceding a sustained interruption. MAIFI = Total number of customer momentary interruption events / Total number of PGE customers served on feeders with MV90 or SCADA ------------------------------------------------------------------------------------------------------------------------------------------------ CAIDI is the customer average interruption duration index. Once an outage occurs, this index is the average time to restore service to the customer. It is determined by dividing the annual sum of all customer sustained interruption durations by the total annual number of customer sustained interruptions. CAIDI = Sum of customer sustained interruption durations / Total number of customer sustained interruptions CAIDI = SAIDI / SAIFI | [8 empty] | A MED is a day in which the daily system SAIDI exceeds a threshold value, TMED. The SAIDI index is used as the basis of this definition since it leads to consistent results regardless of utility size, and because SAIDI is a good indicator of operational and design stress. Even though SAIDI is used to determine the MEDs, all indices should be calculated based on removal of the identified days. In calculating daily system SAIDI, any interruption that spans multiple days is accrued to the day on which the interruption begins. The MED identification TMED value is calculated at the end of each reporting period (typically one year) for use the next reporting period, as follow: a) Collect values of daily SAIDI for five sequential years, ending on the last day of the last complete reporting period. If fewer than five years of historical data are available, use all available historical data until five years of historical data are available. b) Only those days that have a SAIDI/Day value will be used to calculate TMED (do not include days that did not have any interruptions). c) Take the natural logarithm (ln) of each daily SAIDI value in the dataset. d) Find α (Alpha), the average of the logarithms (also known as the log-average) of the data set. e) Find β (Beta), the standard deviation of the logarithms (also known as the log-standard deviation) of the dataset. f) Compute the MED threshold, TMED using: TMED = g) Any day with daily SAIDI greater than the threshold value TMED that occurs during the subsequent reporting period is classified as a MED. Activities that occur on days classified as MEDs should be separately analyzed and reported.
𝑒^((𝛼+2.5 𝛽))

## Baseline 4.1.b
UM 2005/DSP Requirement
4.1.b | A summary of the utility’s distribution system assets including:
4.1.b.i | Asset classes
4.1.b.v | Number of assets in each class
4.1.b.ii | Average age of assets in each class
4.1.b.iii | Age range of assets in each class
4.1.b.iv | Industry life expectancy of assets in each class
| Table of Contents | Asset dataset as of March 2021
4.1.b.iii - Age range of Assets
|  | 4.1.b.i - Asset Classes | 4.1.b.ii - Average age of Assets | 4.1.b.iv - Average Service Life | 4.1.b.v - # of Assets | 0-9 | 10-19 | 20-29 | 30-39 | 40-49 | 50-59 | 60-69 | 70-79 | 80-89 | 90-99 | 100+ | Unknown
|  | Substation Structures | n/a | 65 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
|  | Substation Transformers | 38 | 55 | 407 | 31 | 47 | 79 | 28 | 78 | 44 | 44 | 15 | 10 | 1 | 0 | 30
|  | Circuit Breakers | 21 | 55 | 1617 | 497 | 280 | 335 | 32 | 106 | 72 | 75 | 6 | 0 | 0 | 0 | 214
|  | Other Substation Equipment | 30 | 65 | 9967 | 1075 | 1107 | 1490 | 192 | 891 | 924 | 211 | 48 | 1 | 0 | 111 | 3917
|  | Distribution Poles | 41 | 48 | 203615 | 20346 | 18717 | 23809 | 26026 | 34514 | 32696 | 31619 | 13636 | 1385 | 315 | 33 | 519
|  | OH Transformers | 29 | 50 | 108500 | 29962 | 16906 | 12573 | 7335 | 15098 | 13421 | 10259 | 2330 | 198 | 15 | 4 | 399
|  | Reclosers and Sectionalizers | 8 | 50 | 422 | 256 | 160 | 2 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 2
|  | Voltage Regulators | 9 | 50 | 55 | 29 | 18 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
|  | Capacitor Banks | 27 | 50 | 689 | 69 | 103 | 229 | 239 | 46 | 0 | 0 | 0 | 0 | 0 | 2 | 1
|  | Other OH Conductor Devices | 21 | 48 | 175492 | 48 | 13 | 3964 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171466
|  | UG Transformers | 28 | 55 | 71153 | 2405 | 17943 | 21228 | 11722 | 13988 | 3569 | 135 | 15 | 0 | 1 | 4 | 143
|  | UG Conduit | 12 | 80 | 243273 | 88824 | 109031 | 36544 | 630 | 449 | 202 | 4 | 1 | 0 | 0 | 0 | 7588
|  | Other UG Conductor Devices | 19 | 55 | 3411 | 149 | 624 | 1937 | 22 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 667
|  | Parameters: |  |  | For distribution poles:
|  | 1. Age based on manufacture year from Maximo (pulled from ODS) unless noted 2. Only assets in service in 2020 included • Currently IN SERVICE status and manufactured in or before 2020 • RETIRED status and status date after 2020 • If from GIS, all current features assumed to be in service 3. Asset manufactured in 2020 considered to be 1 year old 4. NULL or manufacture year/install year < 1911 ignored for average and considered unknown age bucket |  |  | 1. Age based on installation date in GIS (source as-built or field correction) 2. Only poles in service in 2020 included • Currently in service in or before 2020 • Any installation date < 01/01/1911 or > 12/31/2019 considered unkown and excluded for average 3. Rounded average age to nearest year 4. Only PGE owned poles included 5. Removed (not considered distribution) • Non-wood street light pole • Wood street light pole • Wood wild life pole • Tree 6. Did not include transmission pole with distribution underbuild
Note on E19: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Reclosers are assets in Maximo but the manufacture data appears to be faulty (all reclosers manufactured in the year 2000). Using install date from GIS TD.DynamicProtectiveDevice where subtype <> 1
Note on E20: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Regulators are assets in Maximo but the Voltage regulators are in Maximo but manufacture data appears to be faulty (mostly null or 2000). Using install date from GIS TD.VoltageRegulator
Note on E21: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: distribution capacitor banks aren't in Maximo. Using GIS install date and asset count from TD.PFCorrectingEquipment.
Note on E24: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: distribution conduit isn't an asset in Maximo. Using GIS install date and asset count from TD.Conduitsystem. As a linear asset not sure if count makes sense

## Baseline 4.1.c - SCADA
UM 2005/DSP Requirement
4.1.c | A discussion of distribution system monitoring and control capabilities including:
4.1.c.i | Number of feeders
4.1.c.ii | Number of substations
4.1.c.iii | Monitoring and control technologies (such as SCADA, AMI, etc.) currently installed, and the percentage of substations, feeders, and other applicable equipment with each technology
4.1.c.iv | A description of the monitoring and control capabilities (for example, percentage of system with each technology, resulting capacity, such as remote fault detection or power quality monitoring, and what time interval measurements are available)
| Table of Contents | SCADA dataset as of March 2021
[5 empty] | 4.1.c.ii Substation | Substation ID | Classificaton | 4.1.c.iii SCADA Type | 4.1.c.iii SCADA Protocol | In Service? | Distribution Substation? | SCADA Deployed Distribution?
|  | 4.1.c.iii | 153 | Total Distribution Subtations | ABERNETHY | ABRN | D | 4 | DNP | TRUE | TRUE | TRUE
|  | 4.1.c.iii | 124 | Total SCADA Deployed | ALDER | ALDR | D | 4 | DNP | TRUE | TRUE | TRUE
|  | 4.1.c.iii | 81.05% | Percent Deployment | AMITY | AMTY | D | MV90 | N/A | TRUE | TRUE | FALSE
[5 empty] | ARLETA | ARLT | D | MV90 | N/A | TRUE | TRUE | FALSE
|  | 4.1.c.iii |  | If a substation has SCADA, then we assume all feeders in that substation have the same SCADA as well. | BANKS | BNKS | D | 4 | DNP | TRUE | TRUE | TRUE
[5 empty] | BARNES | BRNS | D | MV90 | N/A | TRUE | TRUE | FALSE
[5 empty] | BEAVERTON | BVRT | D | 1 | L&G8979 | TRUE | TRUE | TRUE
|  | 4.1.c.i |  | Will manually create based on this table and Distribution Planning feeder spreadsheet, not yet complete | BELL | BELL | D | 4 | DNP | TRUE | TRUE | TRUE
[5 empty] | BETHANY | BTHY | D | 2 | L&G8979 | TRUE | TRUE | TRUE
[5 empty] | BETHEL | BTHL | T&D | 2 | L&G8979 | TRUE | TRUE | TRUE
|  | 4.1.c.iv |  | SCADA Type/SCADA Protocol data time intervals | BLUE LAKE | BLLK | T&D | 2 | DNP | TRUE | TRUE | TRUE
|  |  |  | 1. DNP: | BOONES FERRY | BFRY | D | 2 | DNP | TRUE | TRUE | TRUE
|  |  |  | a. 2 Sec – Status exception polling | BORING | BRNG | D | 2 | L&G8979 | TRUE | TRUE | TRUE
|  |  |  | b. 10 Sec – Analog Full Scan | BRIGHTWOOD | BTWD | D | 4 | DNP | TRUE | TRUE | TRUE
|  |  |  | c. 30 Sec – Status Full / Integrity Scan | BROOKWOOD | BKWD | D | 2 | L&G8979 | TRUE | TRUE | TRUE
|  |  |  | d. 1 hr – Accumulator Read | BUTLER | BTLR | D | 4 | DNP | TRUE | TRUE | TRUE
|  |  |  | 2. TeleGyr (L&G 8979) | CANBY | CNBY | D | MV90 | N/A | TRUE | TRUE | FALSE
|  |  |  | a. 2 Sec – Status full scan | CANEMAH | CNMH | T | 2 | DNP | TRUE | FALSE | FALSE
|  |  |  | b. 10 Sec – Analaog Full Scan | CANYON | CNYN | D | 2 | L&G8979 | TRUE | TRUE | TRUE
|  |  |  | c. 1 Hr – Accumulator scan | CARTY SUBSTATION | CRTY | D | 4 | DNP | FALSE | FALSE | FALSE
|  |  |  | 3. MV90 | CARVER | CRVR | T&D | 3 | L&G8979 | TRUE | TRUE | TRUE
|  |  |  | a. Once a week | CASCADE | CSCD | D | NON-SCADA | N/A | TRUE | TRUE | FALSE
[5 empty] | CEDAR HILLS | CHLS | D | 2 | L&G8979 | TRUE | TRUE | TRUE
[5 empty] | CENTENNIAL | CNTL | D | MV90 | N/A | TRUE | TRUE | FALSE
[5 empty] | CENTURY | CTRY | D |  |  | FALSE | FALSE | FALSE
[5 empty] | CLACKAMAS | CLCK | D | 2 | L&G8979 | TRUE | TRUE | TRUE
[5 empty] | CLAXTAR | CLXT | D | MV90 | N/A | TRUE | TRUE | FALSE
[5 empty] | COFFEE CREEK | CCRK | D | 3 | L&G8979 | TRUE | TRUE | TRUE
[5 empty] | COLTON | CLTN | D | 2 | L&G8979 | TRUE | TRUE | TRUE
[5 empty] | CORNELIUS | CNLS | D | 2 | L&G8979 | TRUE | TRUE | TRUE
[5 empty] | CORNELL | CRNL | D | 4 | DNP | TRUE | TRUE | TRUE
[5 empty] | CULVER | CLVR | D | 4 | DNP | TRUE | TRUE | TRUE
[5 empty] | CURTIS | CRTS | D | 4 | DNP | TRUE | TRUE | TRUE
[5 empty] | DAYTON | DYTN | D | 2 | L&G8979 | TRUE | TRUE | TRUE
[5 empty] | DELAWARE | DLWR | D | 4 | DNP | TRUE | TRUE | TRUE
[5 empty] | DENNY | DNNY | D | 2 | L&G8979 | TRUE | TRUE | TRUE
[5 empty] | DILLEY | DLLY | D | 4 | DNP | TRUE | TRUE | TRUE
[5 empty] | DUNNS CORNER | DNCR | D | 2 | L&G8979 | TRUE | TRUE | TRUE
[5 empty] | DURHAM | DRHM | D | 2 | L&G8979 | TRUE | TRUE | TRUE
[5 empty] | E | ESUB | D | 2 | L&G8979 | TRUE | TRUE | TRUE
[5 empty] | EAGLE CREEK | ECRK | D | MV90 | N/A | TRUE | TRUE | FALSE
[5 empty] | EASTPORT | EPRT | D | 4 | DNP | TRUE | TRUE | TRUE
[5 empty] | ELMA | ELMA | D | 4 | DNP | TRUE | TRUE | TRUE
[5 empty] | ESTACADA | ESTC | D | 4 | DNP | TRUE | TRUE | TRUE
[5 empty] | EVERGREEN | EVGN | T |  |  | FALSE | FALSE | FALSE
[5 empty] | FAIRMOUNT | FMNT | D | MV90 | N/A | TRUE | TRUE | FALSE
[5 empty] | FAIRVIEW | FRVW | D | 4 | DNP | TRUE | TRUE | TRUE
[5 empty] | FARADAY | FRDY | T | 4 | DNP | TRUE | FALSE | FALSE
[5 empty] | FARGO | FRGO | D | MV90 | N/A | TRUE | TRUE | FALSE
[5 empty] | FORT ROCK | FRCK | T | NON-SCADA | N/A | TRUE | FALSE | FALSE
[5 empty] | GALES CREEK | GCRK | D | 4 | DNP | TRUE | TRUE | TRUE
[5 empty] | GARDEN HOME | GRDH | D | 4 | DNP | TRUE | TRUE | TRUE
[5 empty] | GLENCOE | GLNC | D | MV90 | N/A | TRUE | TRUE | FALSE
[5 empty] | GLENCULLEN | GLCL | D | MV90 | N/A | TRUE | TRUE | FALSE
[5 empty] | GLENDOVEER | GLDV | D | 4 | DNP | TRUE | TRUE | TRUE
[5 empty] | GLISAN | GLSN | D | 4 | DNP | TRUE | TRUE | TRUE
[5 empty] | GRAND RONDE | GRND | D | 2 | L&G8979 | TRUE | TRUE | TRUE
[5 empty] | GRESHAM | GRSH | T | 4 | DNP | TRUE | FALSE | FALSE
[5 empty] | HARBORTON | HRBT | T&D | 4 | DNP | TRUE | TRUE | TRUE
[5 empty] | HARMONY | HRMY | D | 2 | L&G8979 | TRUE | TRUE | TRUE
[5 empty] | HARRISON | HRSN | D | 4 | DNP | TRUE | TRUE | TRUE
[5 empty] | HAYDEN ISLAND | HYDN | D | 4 | DNP | TRUE | TRUE | TRUE
[5 empty] | HELVETIA | HLVT | D | 4 | DNP | FALSE | FALSE | FALSE
[5 empty] | HEMLOCK | HMLK | D | 2 | L&G8979 | TRUE | TRUE | TRUE
[5 empty] | HILLCREST | HLCR | D | 4 | DNP | TRUE | TRUE | TRUE
[5 empty] | HILLSBORO | HLBR | D | 3 | L&G8979 | TRUE | TRUE | TRUE
[5 empty] | HOGAN NORTH | HGNN | D | 2 | L&G8979 | TRUE | TRUE | TRUE
[5 empty] | HOGAN SOUTH | HGNS | D | 2 | L&G8979 | TRUE | TRUE | TRUE
[5 empty] | HOLGATE | HLGT | D | MV90 | N/A | TRUE | TRUE | FALSE
[5 empty] | HORIZON | HRZN | T | 4 | DNP | TRUE | FALSE | FALSE
[5 empty] | HUBER | HUBR | D | 2 | L&G8979 | TRUE | TRUE | TRUE
[5 empty] | INDIAN | INDN | D | 3 | L&G8979 | TRUE | TRUE | TRUE
[5 empty] | ISLAND | ISLD | D | 2 | L&G8979 | TRUE | TRUE | TRUE
[5 empty] | JENNINGS LODGE | JLDG | D | MV90 | N/A | TRUE | TRUE | FALSE
[5 empty] | KELLEY POINT | KLPT | D | 3 | DNP | TRUE | TRUE | TRUE
[5 empty] | KELLY BUTTE | KLBT | D | 3 | L&G8979 | TRUE | TRUE | TRUE
[5 empty] | KING CITY | KNGC | D | 4 | DNP | TRUE | TRUE | TRUE
[5 empty] | LELAND | LLND | D | 2 | L&G8979 | TRUE | TRUE | TRUE
[5 empty] | LENTS | LNTS | D | 2 | L&G8979 | TRUE | TRUE | TRUE
[5 empty] | LIBERAL | LBRL | D | 2 | L&G8979 | TRUE | TRUE | TRUE
[5 empty] | LIBERTY | LBRT | D | 4 | DNP | TRUE | TRUE | TRUE
[5 empty] | MAIN | MAIN | D | 2 | L&G8979 | TRUE | TRUE | TRUE
[5 empty] | MARKET | MRKT | D | 2 | L&G8979 | TRUE | TRUE | TRUE
[5 empty] | MARQUAM | MRQM | D | 4 | DNP | TRUE | TRUE | TRUE
[5 empty] | MCCLAIN | MCCL | D | 2 | L&G8979 | TRUE | TRUE | TRUE
[5 empty] | MCGILL | MCGL | D | 4 | DNP | TRUE | TRUE | TRUE
[5 empty] | MCLOUGHLIN | MCLO | T&D | 3 | L&G8979 | TRUE | TRUE | TRUE
[5 empty] | MERIDIAN | MRDN | D | 2 | L&G8979 | TRUE | TRUE | TRUE
[5 empty] | MIDDLE GROVE | MDGR | D | 2 | L&G8979 | TRUE | TRUE | TRUE
[5 empty] | MIDWAY | MDWY | D | MV90 | N/A | TRUE | TRUE | FALSE
[5 empty] | MILL CREEK | MCRK | D | 3 | L&G8979 | TRUE | TRUE | TRUE
[5 empty] | MOLALLA | MOLA | D | 2 | L&G8979 | TRUE | TRUE | TRUE
[5 empty] | MONITOR | MNTR | T | 2 | L&G8979 | TRUE | FALSE | FALSE
[5 empty] | MT ANGEL | MTAN | D | 4 | DNP | TRUE | TRUE | TRUE
[5 empty] | MT PLEASANT | MTPL | D | MV90 | N/A | TRUE | TRUE | FALSE
[5 empty] | MULINO | MLNO | D | MV90 | N/A | TRUE | TRUE | FALSE
[5 empty] | MULTNOMAH | MULT | D | MV90 | N/A | TRUE | TRUE | FALSE
[5 empty] | MURRAYHILL | MRHL | T&D | 2 | L&G8979 | TRUE | TRUE | TRUE
[5 empty] | NEWBERG | NBRG | D | 2 | L&G8979 | TRUE | TRUE | TRUE
[5 empty] | NORTH MARION | NMRN | D | 2 | L&G8979 | TRUE | TRUE | TRUE
[5 empty] | NORTH PLAINS | NPLN | D | 2 | L&G8979 | TRUE | TRUE | TRUE
[5 empty] | NORTHERN | NTRN | D | MV90 | N/A | TRUE | TRUE | FALSE
[5 empty] | OAK GROVE PLANT | OGP1 | T&G | 4 | DNP | TRUE | FALSE | FALSE
[5 empty] | OAK HILLS | OHLS | D | 3 | L&G8979 | TRUE | TRUE | TRUE
[5 empty] | ORENCO | ORNC | D | 3 | L&G8979 | TRUE | TRUE | TRUE
[5 empty] | ORIENT | ORNT | D | 4 | DNP | TRUE | TRUE | TRUE
[5 empty] | OSWEGO | OSWG | D | 3 | L&G8979 | TRUE | TRUE | TRUE
[5 empty] | OXFORD | OXFD | D | 2 | L&G8979 | TRUE | TRUE | TRUE
[5 empty] | PENINSULA PARK | PPRK | D | 4 | DNP | TRUE | TRUE | TRUE
[5 empty] | PLEASANT VALLEY | PVLY | D | 3 | L&G8979 | TRUE | TRUE | TRUE
[5 empty] | PORTSMOUTH | PMTH | D | 2 | L&G8979 | TRUE | TRUE | TRUE
[5 empty] | PROGRESS | PRGS | D | 3 | L&G8979 | TRUE | TRUE | TRUE
[5 empty] | RALEIGH HILLS | RHLS | D | 2 | L&G8979 | TRUE | TRUE | TRUE
[5 empty] | RAMAPO | RAMP | D | 3 | L&G8979 | TRUE | TRUE | TRUE
[5 empty] | REDLAND | RDLD | D | MV90 | N/A | TRUE | TRUE | FALSE
[5 empty] | REEDVILLE | RDVL | D | 4 | DNP | TRUE | TRUE | TRUE
[5 empty] | RHODODENDRON | RHDN | D | NON-SCADA | N/A | TRUE | TRUE | FALSE
[5 empty] | RIVER MILL SWYD | RMSY | D | NON-SCADA | N/A | TRUE | TRUE | FALSE
[5 empty] | RIVERGATE | RVGT | T | 4 | DNP | TRUE | FALSE | FALSE
[5 empty] | RIVERGATE SOUTH | RVGS | D | 2 | L&G8979 | TRUE | TRUE | TRUE
[5 empty] | RIVERVIEW | RVVW | D | 2 | L&G8979 | TRUE | TRUE | TRUE
[5 empty] | ROCK CREEK | RKCK | D | 4 | DNP | TRUE | TRUE | TRUE
[5 empty] | ROCKWOOD | RKWD | D | 2 | L&G8979 | TRUE | TRUE | TRUE
[5 empty] | ROSEMONT | RSMT | D | 4 | DNP | TRUE | TRUE | TRUE
[5 empty] | ROSEWAY | RSWY | D | 4 | DNP | TRUE | TRUE | TRUE
[5 empty] | ROUND BUTTE | RDBT | T | 4 | DNP | TRUE | FALSE | FALSE
[5 empty] | RUBY | RUBY | D | 4 | DNP | TRUE | TRUE | TRUE
[5 empty] | SALEM | SALM | D | 4 | DNP | TRUE | TRUE | TRUE
[5 empty] | SAND SPRING | SSPG | T | NON-SCADA | N/A | TRUE | FALSE | FALSE
[5 empty] | SANDY | SNDY | D | 2 | L&G8979 | TRUE | TRUE | TRUE
[5 empty] | SCAPPOOSE | SCPS | J | MV90 | N/A | TRUE | FALSE | FALSE
[5 empty] | SCHOLLS FERRY | SFRY | D | 4 | DNP | TRUE | TRUE | TRUE
[5 empty] | SCOGGINS | SCGN | D | 2 | L&G8979 | TRUE | TRUE | TRUE
[5 empty] | SCOTTS MILLS | SMLL | D | MV90 | N/A | TRUE | TRUE | FALSE
[5 empty] | SELLWOOD | SLWD | D | 2 | L&G8979 | TRUE | TRUE | TRUE
[5 empty] | SHERIDAN | SHDN | D | 4 | DNP | TRUE | TRUE | TRUE
[5 empty] | SHERWOOD | SHWD | T | 3 | L&G8979 | TRUE | FALSE | FALSE
[5 empty] | SHUTE | SHTE | D | 4 | DNP | TRUE | TRUE | TRUE
[5 empty] | SILVERTON | SLVR | D | 4 | DNP | TRUE | TRUE | TRUE
[5 empty] | SIX CORNERS | SXCR | D | 2 | L&G8979 | TRUE | TRUE | TRUE
[5 empty] | SPRINGBROOK | SPBK | D | 4 | DNP | TRUE | TRUE | TRUE
[5 empty] | ST HELENS | STHL | J | 4 | DNP | TRUE | FALSE | FALSE
[5 empty] | ST LOUIS | STLS | D | 3 | L&G8979 | TRUE | TRUE | TRUE
[5 empty] | ST MARYS EAST | STME | D | 3 | L&G8979 | TRUE | TRUE | TRUE
[5 empty] | ST MARYS WEST | STMW | T | 4 | DNP | TRUE | FALSE | FALSE
[5 empty] | SULLIVAN | SLVN | D | 2 | L&G8979 | TRUE | TRUE | TRUE
[5 empty] | SUMMIT | SMMT | D | 4 | DNP | TRUE | TRUE | TRUE
[5 empty] | SUNSET | SNST | D | 4 | DNP | TRUE | TRUE | TRUE
[5 empty] | SWAN ISLAND | SWNI | D | 2 | L&G8979 | TRUE | TRUE | TRUE
[5 empty] | SYCAN | SYCN | T | NON-SCADA | N/A | TRUE | FALSE | FALSE
[5 empty] | SYLVAN | SYLV | D | MV90 | N/A | TRUE | TRUE | FALSE
[5 empty] | TABOR | TABR | D | 2 | L&G8979 | TRUE | TRUE | TRUE
[5 empty] | TEKTRONIX | TKTX | D | 2 | L&G8979 | TRUE | TRUE | TRUE
[5 empty] | TIGARD | TGRD | D | 3 | L&G8979 | TRUE | TRUE | TRUE
[5 empty] | TONQUIN | TNQN | T&D | 4 | DNP | FALSE | FALSE | FALSE
[5 empty] | TOWN CENTER | TWNC | D | 4 | DNP | TRUE | TRUE | TRUE
[5 empty] | TROJAN | TRJN | T | 2 | L&G8979 | TRUE | FALSE | FALSE
[5 empty] | TUALATIN | TLTN | D | 3 | L&G8979 | TRUE | TRUE | TRUE
[5 empty] | TURNER | TRNR | D | MV90 | N/A | TRUE | TRUE | FALSE
[5 empty] | TWILIGHT | TWLT | D | 2 | L&G8979 | TRUE | TRUE | TRUE
[5 empty] | UNIONVALE | UNVL | D | MV90 | N/A | TRUE | TRUE | FALSE
[5 empty] | UNIVERSITY | UNIV | D | MV90 | N/A | TRUE | TRUE | FALSE
[5 empty] | URBAN | URBN | D | 2 | L&G8979 | TRUE | TRUE | TRUE
[5 empty] | WACKER | WCKR | D | 4 | DNP | TRUE | TRUE | TRUE
[5 empty] | WACONDA | WCND | D | 2 | L&G8979 | TRUE | TRUE | TRUE
[5 empty] | WALLACE | WLLC | D | 4 | DNP | TRUE | TRUE | TRUE
[5 empty] | WELCHES | WLCH | D | 4 | DNP | TRUE | TRUE | TRUE
[5 empty] | WEST PORTLAND | WPRT | D | 4 | DNP | TRUE | TRUE | TRUE
[5 empty] | WEST UNION | WUNI | D | 4 | DNP | TRUE | TRUE | TRUE
[5 empty] | WILLAMINA | WLMN | D | 2 | L&G8979 | TRUE | TRUE | TRUE
[5 empty] | WILLBRIDGE | WLBR | D | MV90 | N/A | TRUE | TRUE | FALSE
[5 empty] | WILSONVILLE | WLSV | D | 4 | DNP | TRUE | TRUE | TRUE
[5 empty] | WOODBURN | WDBN | D | 3 | L&G8979 | TRUE | TRUE | TRUE
[5 empty] | YAMHILL | YMHL | D | MV90 | N/A | TRUE | TRUE | FALSE

## Baseline 4.1.c - AMI
UM 2005/DSP Requirement
4.1.c | A discussion of distribution system monitoring and control capabilities including:
4.1.c.i | Number of feeders
4.1.c.ii | Number of substations
4.1.c.iii | Monitoring and control technologies (such as SCADA, AMI, etc.) currently installed, and the percentage of substations, feeders, and other applicable equipment with each technology
4.1.c.iv | A description of the monitoring and control capabilities (for example, percentage of system with each technology, resulting capacity, such as remote fault detection or power quality monitoring, and what time interval measurements are available)
| Table of Contents | AMI dataset as of March 2021
|  | 4.1.c.iii |  |  | • Time from last gasp to PGE being notified meter is out When an outage occurs in the field, the meter waits 120 seconds and if power is restored in that time, it logs it as a momentary outage, or “click”. If the power is not restored after 120 seconds, the meter sends a power fail alarm which is received by our software within a few seconds. It is then forwarded in real time to Outage Management and Customer Text Alerts within seconds. • Time from meter back on to PGE notified its back on When energized, the meter waits 60 seconds to confirm it’s not a temp restore, and then sends a Power Restore message. This is received by the AMI software and forwarded to Outage Management and Customer Text Alerts within seconds. • How AMI meters handle partial outages (3 phase, etc) On a single phase meter, a partial outage will generally be reported with a low voltage alarm, because instead of the expected ~240 volts, the meter is reporting ~120 volts. On a 3 phase meter, if the phase that powers the actual meter is out, the meter will send a power fail alarm. If one of the other phases is out, the meter will send a single phase fail alarm. • In addition to on/off, what other AMI features are we taking full advantage of (usage measurement, disconnect, tamper notifications, voltage, etc) o We take advantage of remote disconnect/connect along with usage and generation measurements for billing, load research, ESS and Energy Imbalance market settlements, unbilled revenue, etc. In addition: o Hot Socket Alarms - PGE rolls trucks to “hot socket” alarms, which occur when the meter gets above 85 degrees Celsius. In many cases these are due to a meter base issue (in need of customer repair) or increased load at the site (grow operations, etc). o Tamper alarms – PGE rolls a truck to unexpected tamper alarms, e.g. no existing work order driving a field visit from PGE. Many times these are false alarms created by electricians, but there are cases of theft/illegal tamper. o Grid Monitoring – we have begun using AMI meters as a grid monitoring sensor within the last year, specifically for large generation sites like Qualified Facilities or Community Solar. We send a feed of data over to PI (monitoring tool used by T&D) to create visibility for the grid operators to large scale generation occurring in our grid. o Voltage Pinging – We built a systematic voltage pinging program and goes feeder by feeder and pings groups of meters every 15 minutes. This is currently being leveraged by the data science and GIS teams to create drive GIS connectivity corrections, but could be used in the future for Conservation Voltage Reduction programs along with Theft Detection analytics. o Transformer Loading – Last year our team built a transformer loading analytics tool into one of the systems we maintain (Smart Meter Toolbox). Allow the 100+ DPMs and Engineers to enter a transformer and see the aggregate load of all customers, for overloading analysis, capacity planning for new connects and EV, etc. We are working with data science and engineering to finalize a broader, top down, system scan approach for overloaded transformers. This is in DEV and should be live in Q2. • What opportunities do you see to better leverage AMI, both Residential and Business o Residential • Proactive power quality notification for half outs, flickering lights, etc. • More meter status visibility for CSRs, could help with outage calls, program enrollment eligibility, etc. • Enhanced customer web portal, i.e. Energy Tracker 2.0. Show more than just usage, but potential to include generation, outage/alarm history, meter status (ON/OFF) etc. • Prepaid Metering – For customers with remote disconnect meters, we could offer prepaid metering which offers some benefits to customer and utility. Pay as you go approach like filling a gas tank, rather than the typical, deposit>use>bill>pay monthly approach. o Commercial • Demand / Rate Migration alerts • Proactive power quality notifications, single phase outs, phase imbalance • Power Quality Monitoring. Some larger customers are purchasing iGrid to monitor their power quality which is costly to them and PGE. We could offer “iGrid lite” with current meters and some web dev, or, a more robust solution with a new meter and some data science, engineering support. • Controllable Campus Lighting leveraging smart streetlights and our AMI network • Water Meter Network, i.e. offer cities our AMI network to read their water meters so they don’t have to read manually. We have capacity and have successfully demo’d this capability with City of Wilsonville. They would have to use Sensus water meters. • Conversation Voltage Reduction – opportunity to use meter data to reduce substation voltage, especially during peak load, high cost times of day, effectively reducing customer bills and utility power costs. • Theft detection using voltage • GIS and AMI integration for field crews, allow for near real time visibility to customers ON/OFF during outage restoration.
Total PGE meters (and breakdown between RCI)
|  | Meter Type | Count
|  | Residential | 794000
|  | Commercial | 103000
|  | Industrial (>1MW) | 300
|  | Irrigation | 4150
|  | Vacant | 15000
|  | Total | 916450
PGE Meter Types
|  | Manufacturer | Comms | Count
|  | Elster | Sensus | 59000
|  | L+G | Sensus | 45000
|  | Sensus | Sensus | 812000
|  | Elster (opt out) | None | 150
|  | Various | Mv90 | 300
|  | Total |  | 916450
Total AMI meters with remote disconnect capability (and breakdown between RCI)
|  | R/D Meter Type | Count
|  | Commercial | 1500
|  | Residential | 256000
|  | Total | 257500
# of AMI meters that are outside of reliable RF range and must be manually checked
|  | Year | Manual Reads
|  | 2021 | 1218
|  | 2020 | 2423
|  | 2019 | 3498
|  | 2018 | 3616
|  | 2017 | 6108
Here are a few additional details:
15,000 bidirectional meters (solar customers, etc)
47 large generation meters (QF, Community Solar) with a near real time feed of generation data into PI (grid monitoring).
660 primary voltage and 13 sub-transmission voltage meters
635 Direct Access meters (power provided by ESS)
36 Generation Curtailment meters (solar installs where PGE has the ability to stop backfeed)

## Baseline 4.1.d
UM 2005/DSP Requirement
4.1.d | A discussion of any advanced control and communication systems (for example: distribution management systems, distributed energy resources management systems, demand response management systems, outage management systems, field area networks, etc.). Include a description of system visibility and capabilities, the percentage of system reached with each capability, the percentage of customers reached with each capability, and any utility programs utilizing each capability.
| Table of Contents | Advanced control/communication dataset as of March 2021
|  | System | Description of system visibility and capabilities | Percentage of system reached with each capability | Percentage of customers reached with each capability | Any utility programs utilizing each capability
|  | 1. ADMS (Advanced Distribution Management System) | Advanced Distribution Management System (ADMS) – Provides SCADA controls for distribution circuits, automated self-healing circuit functionality (FLISR), assisted/automated switching for planned and unplanned outages, grid optimization, real-time power system studies and, reporting capabilities. Advanced functions includes conservation voltage reduction, volt var optimization, protection analysis, adaptive protection. Mobile Grid Operations is advanced ADMS capability that provides field personnel access to grid data and the ability to update the grid information. | Load Trasfer, Microgrid Ops, Device Management, Load Shed, Feeder Reconfiguration, Low Voltage Analysis, FLISR/VVC, Overload Switching, Intelligent Alarms, Relay Protection, Adaptive Protection, Optimal Power Flow, Feeder Balancing/Rebalancing, Breaker/Fuse Capacity Analysis, Switch Order Management, State Estimation, Secondary Power Flow, Short Term Load Forecast, Energy Losses, Short Circuit Duty Analytis FLISR - 3 Feeders using YFA CVR - 0% Control and Operations - 100% of Feeders (~690 Feeders) | FLISR - 3 ~3000 customers CVR -0% Control and Operations - 100% 12 Feeders are in CVR pilot (2013) | 0
|  | 2. DERMS (Distribution Energy Resources Management System) | DER Management System (DERMS) – Optimally manages and dispatches DERs to provide grid services, facilitates non-wires alternatives, enables DERs to participate in markets, manages smart inverters, and cost-effectively manages distribution deferral resources. DERMS enables enhanced situational awareness under increasing DER penetration by providing DER modeling, aggregation and grouping. The DERMS also enhances the utilization of DER by providing DER forecast, communication and dispatch. | Enterprise DERMS Operational in 2022 | MFWH - 4000 Customers Enterprise DERMS Operational in 2022 | 0
|  | 3. DRMS (Demand Response Management System) | Demand Response Management System (DRMS) : DRMS is a crucial arrangement for balancing energy supply with consumption requirement and stabilizing load on grids during peak hours. An automated demand response is established on AMI, which builds an integrated network between the customers participating in the DR program and the utility for exchanging signals and communicating in real time.new class of management systems that maintains | Solication, Registration, Interconnection, DER portfolio Optimization, Constraint Management, Aggregation functions, Microgrid Management, Islandng, OPF, Dispatch and Schedule |  | Residential PV*​ TBD​ Residential Battery*​ 200 of 500​ Residential EV*​ 100​ Residential T-stat*​ 500​ Ductless Heat Pump​ 50-100​ Multi Family Water Heater (MFWH)*​ TBD​ Single Family Water Heater (SFWH)​ 70-150​ Peak Time Rebate*​ 17,000​ Beaverton Microgrid​ NA​ Anderson Microgrid​ NA​ E-Fleet Platform​ NA​
|  | 4. OMS (Outage Management System) | Ouage Management System (OMS): OMS is a asset/work management system that provides the PGE grid operations the ability to monitor and oeprate the grid while returning power to the customers in cases of outages; Prediction of location of transformer, fused, recloser or breaker that opened upon failure. Prioritizing restoration efforts and managing resources based upon criteria such as locations of emergency facilities, size of outages, and duration of outages. Providing information on extent of outages and number of customers impacted to management, media and regulators. Calculation of estimation of restoration times. Management of crews assisting in restoration. Calculation of crews required for restoration. | Outage Management Operational - all Feeders | 100% of all customers are being monitored
|  | 5. FAN (Field Area Network) | Field Area Network: PGE expects FAN will provide secure, ubiquitous communications to existing Distribution Automation (DA) assets as well as all emerging Distributed Energy Resources (DERs). PGE believes that this new FAN will deliver capabilities necessary for the safe, reliable, and affordable operation of the electric grid. | Field Area Network - 30 Sites | Customer cannot be calculated
|  | 6. DA (Distribution Automation) | Distribution Automation (DA) - Distribution automation (DA) uses digital sensors and switches with advanced control and communication technologies to automate feeder switching; voltage and equipment health monitoring; and outage, voltage, and reactive power management. Automation can improve the speed, cost, and accuracy of these key distribution functions to deliver reliability improvements and cost savings to customers. | Viper is being installed; Sentient MM3+ is being installed | Deriving the customer served, will update in the next cycle

## Baseline 4.1.e
UM 2005/DSP Requirement
4.1.e | Historical distribution system spending for the past five years, in each category:
4.1.e.i | Age-related replacements and asset renewal
4.1.e.ii | System expansion or upgrades for capacity
4.1.e.iii | System expansion or upgrades for reliability and power quality
4.1.e.iv | New customer projects
4.1.e.v | Grid modernization projects
4.1.e.vi | Metering
4.1.e.vii | Preventative maintenance
| Table of Contents | Distribution spending dataset
|  |  | 2016 | 2017 | 2018 | 2019 | 2020
|  | Age-related replacements and asset renewal | 49154093.18 | 84237345.3 | 85596952.07 | 87070673.08 | 85538736.22 | 4.1.e.i
|  | System expansion or upgrades for capacity | 32435392.48 | 66773761.08 | 81983582.64 | 36838974.2 | 30067022.11 | 4.1.e.ii
|  | System expansion or upgrades for reliability and power quality | 38927621.33 | 51202074.58 | 76168137.08 | 121503276.33 | 84014971.14 | 4.1.e.iii
|  | New customer projects | 50409001.11 | 51666269.21 | 60052181.81 | 86128586.53 | 174938842.63 | 4.1.e.iv
|  | Grid modernization projects | 8935.2 | 1665754.72 | 2672199.62 | 3528966.46 | 4922835.54 | 4.1.e.v
|  | Metering | 9068647.8 | 7480459.92 | 7281769.75 | 11915666.38 | 8613549.19 | 4.1.e.vi
|  | Preventive maintenance | 375739.94 | 4494524.63 | 7754273.73 | 4870318.97 | 2017797.73 | 4.1.e.vii
|  | Grand Total | 180379431.04 | 267520189.44 | 321509096.7 | 351856461.95 | 390113754.56

## Baseline 4.1.f
UM 2005/DSP Requirement
4.1.f | Net Metering and Small Generator information:
4.1.f.i | Total existing net metering facilities and small generator facilities interconnected to the distribution grid (or to the transmission system, as appropriate for small generator facilities) at time of filing, by feeder.
4.1.f.i.1 | The total number of net metering facilities by resource type
4.1.f.i.2 | The total estimated rated generating capacity of net metering facilities by resource type
4.1.f.i.3 | The total number of small generator facilities by resource type
4.1.f.i.4 | The total nameplate capacity of small generator facilities by resource type
4.1.f.ii | The total number and nameplate capacity of queued net metering facilities and small generator facilities at time of filing, by feeder, broken down by resource type
4.1.f.iii | A map, in electronic format, identifying locations of net metering facilities and small generator facilities interconnected to the distribution grid (or to the transmission system, as appropriate for small generator facilities) at time of filing. Map is only accessible to PGE DRP currently. Will show map during May 2021 Partner Meeting and ask for volunteers like we did in TWG meeting. Access can be granted by emailing DSP@pgn.com * include in subject line - access request baseline map * include the following information: first and last name, email, and organization
| Table of Contents | Net Metering & Small Generator dataset as of Jan 2021
|  | 4.1.f.i.1 | In-Service Net Metering | [6 empty] | 4.1.f.i.3 | In-Service Qualified Facilities
|  | Row Labels | Count of Type of Generator | Total | [5 empty] | Row Labels | Count of Type of Generator
|  | Digester Gas | 0.02517% | 3 | [5 empty] | Solar | 41
|  | Fuel Cell | 0.02517% | 3 | [5 empty] | Grand Total | 41
|  | Hydro | 0.05034% | 6
|  | Methane Gas | 0.008391% | 1 | [5 empty] | 4.1.f.i.4 | In-Service Generating Nameplate Capacity Qualified Facilities
|  | Solar | 99.54% | 11863
|  | Solar+Wind | 0.01678% | 2
|  | Wind | 0.3356% | 40
|  | Grand Total | 100% | 11918
|  | 4.1.f.i.2 | In-Service Generating Nameplate Capacity Net Metering
|  | Digester Gas | Fuel Cell | Hydro | Methane Gas | Solar | Solar+Wind | Wind | Grand Total
|  | 2100 | 21 | 184 | 1700 | 105063 | 21 | 649 | 109741
|  | 4.1.f.ii | In Queue Net Metering
|  | Row Labels | Count of Type of Generator
|  | Digester Gas | 1
|  | Methane | 1 | [6 empty] | 4.1.f.ii | In Queue Qualified Facilities
|  | Solar | 563
|  | Grand Total | 565 | [6 empty] | Row Labels | Count of Type of Generator
[10 empty] | Solar | 50
[10 empty] | Grand Total | 50
[6 empty] | Type of Generator | Generating Nameplate
|  | Row Labels | Sum of Total System Capacity kW |  |  | Digester Gas | AC |  |  | Row Labels | Sum of Total System Capacity kW
|  | Digester Gas | 633 |  |  | Fuel Cell | AC |  |  | Solar | 114606.233
|  | Methane | 1200 |  |  | Hydro | AC |  |  | Grand Total | 114606.233
|  | Solar | 10019.463 |  |  | Methane Gas | AC
|  | Grand Total | 11852.463 |  |  | Solar | DC
[6 empty] | Solar+Wind | DC+AC
[6 empty] | Wind | AC
|  | 4.1.f.iii | Screenshot of Baseline Map

## Baseline 4.1.g & h
UM 2005/DSP Requirement
4.1.g | Total number of electric vehicles (EVs) of various sizes served by the utility's system at time of filing
4.1.h | Number of EVs added to the utility's system in each of the last five years
| Table of Contents | EV dataset
Assumptions
|  |  | Parameter |  | Value | Unit | Notes
|  |  | Percent of vehicles sold in current model year |  | 0.75 | % | Vehicles are sold in their model year until the fall. For exmaple 75% of MY2016 vehicles are sold in 2016
|  |  | Percent of vehicles sold in the previous model year |  | 0.25 | % | The next model year goes on sale in the fall of the previous year. For example 25% of MY2017 vehicles are sold in 2016
Analysis
|  |  | Requirement | Parameter | Value | Unit | Notes
|  |  | 4.1.g | Total number of electric vehicles served at time of filing |  |  | Source: Oregon Zero Emissions Vehicle Dashboard (raw data below). Appears to capture all vehicles to-date up to mid 2020.
|  |  |  | Car | 17302 | vehicles
|  |  |  | SUV | 1798 | vehicles
|  |  |  | Truck | 0 | vehicles | Only 1999 and 2001 Ford Rangers counted here, one out of state and one in Lane County
|  |  |  | Van | 279 | vehicles
|  |  |  | Motorcycle | 78 | vehicles
|  |  |  | Moped | 24 | vehicles
|  |  |  | Low-speed Car | 63 | vehicles
|  |  |  | Med-speed Car | 1 | vehicles
|  |  |  | Total | 19545 | vehicles
|  |  | 4.1.h REV 1 | Number of Evs added to the utility's system in last five years | 0 |  | Source: Oregon Zero Emissions Vehicle Dashboard. Appears to capture all vehicles to-date up to mid 2020.
|  |  |  | 2015 | 1757 | vehicles
|  |  |  | 2016 | 2441 | vehicles
|  |  |  | 2017 | 3183 | vehicles
|  |  |  | 2018 | 4014.25 | vehicles
|  |  |  | 2019 | 3176.25 | vehicles
|  |  |  | 2020 | 1162.5 | vehicles | 2020 incomplete.
|  |  |  | 2021 | N/A
|  |  |  | Total | 13977
|  |  | 4.1.h REV 2 | Number of Evs added to the utility's system in last five years | 0 |  | Source: DEQ for purposes of CFC reporting (source material PDF'd in raw data folder)
|  |  |  | 2017 | 1836 | vehicles | "
|  |  |  | 2018 | 3138 | vehicles | "
|  |  |  | 2019 | 3889 | vehicles | "
|  |  |  | 2020 | 2494 | vehicles | Source: DEQ e-mail from Cory Ann Wind on April 6, 2021. Conversation with Cory Ann on April 9 noted that this number is likely incorrect (far too conservative).
|  |  |  | Total | 11357
Assumptions
1. EVs include battery electric vehicles and plug-in hybrid electric vehicles.
2. 294 out-of-state vehicles left out. Unclear if vehicles were purchased out of state and used in Oregon or purchased in Oregon and registered out-of-state.
3. 75% of vehicles are sold in their current model year (for example, 75% of 2015 Nissan Leafs are sold in 2015) and 25% are sold in the previous model year (for example, 25% of 2015 Nissan Leafs are sold in 2014). New model years are generally introduced in the fall.

## Baseline 4.1.i
UM 2005/DSP Requirement
4.1.i | Total number of charging stations on the utility's system, broken down by type, ownership, and feeder
Table of Contents
Data Sources:
For non-PGE owned charging sites, data source is US Alternative Fuel Data Center, filtered for Oregon, and manually matched to sites that are within PGE service area. For PGE-owned sites, source is internal PGE tracking.
Alternative Fuels Data Center database accessed April 1, 2021. Link is available here:
https://afdc.energy.gov/stations#/find/nearest?fuel=ELEC
Caveat about the data: These are DRAFT numbers and have not undergone full QAQC. This will be done leading up to the TE Plan filing and the DSP Part I filing later this year. The data however are indicative of the type of data PGE can provide, and should be mostly accurate. Moreover, the data sources may not capture every charging location in a utility service area given difficulties of accessing private charging data for businesses, and the nature of open-source tools such as the DOE's AFDC.

## Baseline 4.1.j
UM 2005/DSP Requirement
4.1.j | Total number of charging stations added to the utility's system in each of the last five years, broken down by type
4.1.j.1 | Data on the availability and usage patterns of charging stations
| Table of Contents | 4.1.j | 4.1.j.1

## Baseline 4.1.l
UM 2005/DSP Requirement
4.1.l | A high-level summary of demand response (DR) pilot and/or program performance metrics for the past five years including: (For example see Table 26 on page 101 of Appendix 1 of 2019 PGE Smart Grid Report, https://edocs.puc.state.or.us/efdocs/HAQ/um1657haq15635.pdf)
4.1.l.i | Number of customers participating by residential and business customer class, and combined total
4.1.l.ii | By winter and summer demand response season:
4.1.l.ii.1 | Maximum available capacity of DR by residential and business customer class, and combined total
4.1.l.ii.2 | Season system peak
4.1.l.ii.3 | Available capacity of DR, expressed as a percentage of the season system peak
| Table of Contents | Demand Response dataset
[5 empty] | 2016 | 2017 | 2018 | 2019 | 2020
|  |  | # Customers participating in DR | Residential | 16409 | 16370 | 26552 | 107876 | 116835
|  |  |  | Business | 42 | 18 | 43 | 95 | 509
|  |  |  | Total | 16467 | 16388 | 26595 | 107971 | 117344
|  | Winter | Maximum available capacity of DR (MW) | Residential | 1.4 | 0.5 | 5.3 | 17.1 | 17.9
|  |  |  | Business | 14.9 | 3 | 15.2 | 2.7 | 21
|  |  |  | Total | 16.3 | 3.5 | 20.5 | 20 | 38.58
|  |  | Season Peak (MW) |  | 3716 | 3727 | 3399 | 3422 | 3330
|  |  | Available capacity of DR (% of season system peak) |  | 0.44% | 0.1% | 0.6% | 0.5845% | 1.159%
|  | Summer | Maximum available capacity of DR (MW) | Residential | 5.8 | 4.5 | 13 | 32.3 | 39
|  |  |  | Business | 12.9 | 3 | 15.2 | 4.0116 | 23.68
|  |  |  | Total | 18.7 | 7.5 | 28.2 | 36.32 | 62.68
|  |  | Season Peak (MW) |  | 3726 | 3976 | 3816 | 3764 | 3771
|  |  | Available capacity of DR (% of season system peak) |  | 0.5% | 0.19% | 0.74% | 0.9649% | 1.662%